## Intake
Water Efficiency Dashboard
Purpose
Use this tracker to collect, organize, and analyze water efficiency data from your cooling tower over time, and controlled for seasonal changes in cooling demand
Measure the following metrics: (1) water efficiency trends (2) Total use cost of your cooling tower program (3) Total use cost versus budget
Please note: This tracker is for facilities that already have water meters installed on both their makeup and bleed lines
Directions
(1) Only change data in the blue boxes
(2) Example data is pre-populated
(3) To clear example data, either right click and select "Clear Contents" or backspace and retype info
(4) Use the log sheet, below to record your tower meter readings. The tool will automatically adjust to whatever frequency your readings occur
(5) Results populate on the "Dashboard" tab
(6) Any questions or feedback? Please email sales@eaiwater.com
Data Intake
Facility Name
Enter your facility name here
Water Consumption |  |  |  |  | Water Treatment Costs |  |  |  |  | Utility Water Costs
Date | Time | Makeup Reading (gal) | Bleed Reading (gal) | Notes on Water Treamtent Program | Month | Chemicals/ Consumables | Freight/ Delivery | Onsite Service | Bundled Service | Month | Water Billing Rate | Billing Unit | Sewer Billing Rate (incl. any credits) | Billing Unit
2023-01-01 | 14:00 | 46656 | 16662.8571 |  | January | 500 | 100 | 200 | 0 | January | 7.12 | CCF | 5.39 | CCF
2023-01-08 | 13:00 | 97977.6 | 34992 |  | February | 400 | 100 | 200 | 0 | February | 7.12 | CCF | 5.39 | CCF
2023-01-15 | 14:00 | 153964.8 | 53052.3871 | Increased dosing of scale inhibitor | March | 600 | 150 | 200 | 0 | March | 7.12 | CCF | 5.39 | CCF
2023-01-22 | 12:00 | 191289.6 | 65092.6452 | Reprogrammed softener | April |  |  |  |  | April
2023-01-29 | 14:00 | 233280 | 78637.9355 |  | May |  |  |  |  | May
2023-02-05 | 15:00 | 284601.6 | 95193.2903 |  | June |  |  |  |  | June
2023-02-12 | 9:00 | 345254.4 | 109298.5926 |  | July |  |  |  |  | July
2023-02-19 | 14:00 | 401241.6 | 122318.8717 |  | August |  |  |  |  | August
2023-02-26 | 13:45 | 452563.2 | 134254.1275 |  | September |  |  |  |  | September
2023-03-05 | 14:00 | 522547.2 | 150529.4764 |  | October |  |  |  |  | October
2023-03-12 | 14:00 | 597196.8 | 167889.8485 |  | November |  |  |  |  | November
2023-03-19 | 14:00 | 671846.4 | 185250.2206 |  | December |  |  |  |  | December
2023-03-26 | 14:00 | 755827.2 | 204780.6392
2023-04-02 |  |  |  |  | Do you have an budget for water treatment that you need to stay under?
2023-04-09 |  |  |  |  | Yes | Monthly
2023-04-16
2023-04-23 |  |  |  |  | If monthly enter here: |  |  | If annual, enter here:
2023-04-30 |  |  |  |  | January | 800
2023-05-07 |  |  |  |  | February | 800
2023-05-14 |  |  |  |  | March | 900
2023-05-21 |  |  |  |  | April | 1000
2023-05-28 |  |  |  |  | May | 1100
2023-06-04 |  |  |  |  | June | 1400
2023-06-11 |  |  |  |  | July | 1400
2023-06-18 |  |  |  |  | August | 1500
2023-06-25 |  |  |  |  | September | 1800
2023-07-02 |  |  |  |  | October | 1300
2023-07-09 |  |  |  |  | November | 1100
2023-07-16 |  |  |  |  | December | 800
2023-07-23
2023-07-30
2023-08-06
2023-08-13
2023-08-20
2023-08-27
2023-09-03
2023-09-10
2023-09-17
2023-09-24
2023-10-01
2023-10-08
2023-10-15
2023-10-22
2023-10-29
2023-11-05
2023-11-12
2023-11-19
2023-11-26
2023-12-03
2023-12-10
2023-12-17
2023-12-24
2023-12-31

## Calcs_Water (hidden)
|  | Current Month | Latest Reading | Current WE Score | Previous Recording | Previous WE Score | Inc/Dec | Change % | YTD WE Score Average | [6 empty] | Total Budget
|  | March | 2023-03-26 14:00 | 4.3 | 2023-03-19 14:00 | 4.3 | No Change | 8.262e-14% | 3.4846 | [6 empty] | 13900
|  | Current Month Total Spend/1k gal MU | Previous Month Total Spend/1k gal MU | Month -2 Total Spend/1k gal MU | % Change | Average Spend/1k gal YTD | Previous Month - Treatment Share | Previous Month - Utility Share
|  | 14.3263 | 14.5378 | 16.1975 | -10.25% | 15.3009 | 3.1922 | 11.3455
Reading Date | Hour | DTG | Reading Month | Reading Month | Days Since Last | Makeup (gal) | Bleed (gal) | Evap (gal) | Change in Makeup | Change in Bleed | Cycles | WE Score | 1k gal MU | Month | Month | Month | WE Score | MU Useage (monthly) | MU Useage (Cumulative) | 1k gal MU (monthly) | 1k gal MU (cumulative) | Change in Bleed (gal) | Water Rate/ 1k gal | Monthly Water Bill | Sewer Rate/1k gal | Monthly Sewer Bill | Monthly Sewer Spend per 1k gal MU | Monthly Water Treatment Spend | Cumulative Treatment Spend | Monthly Treatment Spend/1k gal MU | Monthly Utility Spend/1k gal MU | Monthly Total Spend | Cumulative Total Spend | Total Monthly Spend/1k gal MU | Average Total Spend/1k gal MU | Monthly Treatment Budget | Cumulative Treatment Budget | Over/Under Monthly | % of Total Budget Consumed | Target Consumption %
2023-01-01 | 14:00 | 2023-01-01 14:00 | 1 | January | 0 | 46656 | 16662.8571 | 29993.1429 | 0 | 0 |  | 0 |  | January | 1 | January | 3.0113 | 186624 | 186624 | 186.624 | 186.624 | 61975.0783 | 9.5181 | 1776.2975 | 7.2054 | 446.5541 | 2.3928 | 800 | 800 | 4.2867 | 11.9109 | 3022.8516 | 3022.8516 | 16.1975 | 16.1975 | 800 | 800 | 0 | 5.755% | 5.755%
2023-01-08 | 13:00 | 2023-01-08 13:00 | 1 | January | 6.9583 | 97977.6 | 34992 | 62985.6 | 51321.6 | 18329.1429 | 2.8 | 2.8 | 51.3216 | February | 2 | February | 3.9428 | 219283.2 | 405907.2 | 219.2832 | 405.9072 | 55616.192 | 9.5181 | 2087.1495 | 7.2054 | 400.7359 | 1.8275 | 700 | 1500 | 3.1922 | 11.3455 | 3187.8854 | 6210.737 | 14.5378 | 15.3009 | 800 | 1600 | 100 | 10.79% | 11.51%
2023-01-15 | 14:00 | 2023-01-15 14:00 | 1 | January | 7.0417 | 153964.8 | 53052.3871 | 100912.4129 | 55987.2 | 18060.3871 | 3.1 | 3.1 | 55.9872 | March | 3 | March | 4.3 | 303264 | 709171.2 | 303.264 | 709.1712 | 70526.5116 | 9.5181 | 2886.4834 | 7.2054 | 508.1704 | 1.6757 | 950 | 2450 | 3.1326 | 11.1937 | 4344.6538 | 10555.3908 | 14.3263 | 14.8841 | 900 | 2500 | -50 | 17.63% | 17.99%
2023-01-22 | 12:00 | 2023-01-22 12:00 | 1 | January | 6.9167 | 191289.6 | 65092.6452 | 126196.9548 | 37324.8 | 12040.2581 | 3.1 | 3.1 | 37.3248 | April | 4 | April |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1000 | 3500 | 1000 | 0% | 25.18%
2023-01-29 | 14:00 | 2023-01-29 14:00 | 1 | January | 7.0833 | 233280 | 78637.9355 | 154642.0645 | 41990.4 | 13545.2903 | 3.1 | 3.1 | 41.9904 | May | 5 | May |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1100 | 4600 | 1100 | 0% | 33.09%
2023-02-05 | 15:00 | 2023-02-05 15:00 | 2 | February | 7.0417 | 284601.6 | 95193.2903 | 189408.3097 | 51321.6 | 16555.3548 | 3.1 | 3.1 | 51.3216 | June | 6 | June |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1400 | 6000 | 1400 | 0% | 43.17%
2023-02-12 | 9:00 | 2023-02-12 09:00 | 2 | February | 6.75 | 345254.4 | 109298.5926 | 235955.8074 | 60652.8 | 14105.3023 | 4.3 | 4.3 | 60.6528 | July | 7 | July |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1400 | 7400 | 1400 | 0% | 53.24%
2023-02-19 | 14:00 | 2023-02-19 14:00 | 2 | February | 7.2083 | 401241.6 | 122318.8717 | 278922.7283 | 55987.2 | 13020.2791 | 4.3 | 4.3 | 55.9872 | August | 8 | August |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1500 | 8900 | 1500 | 0% | 64.03%
2023-02-26 | 13:45 | 2023-02-26 13:45 | 2 | February | 6.9896 | 452563.2 | 134254.1275 | 318309.0725 | 51321.6 | 11935.2558 | 4.3 | 4.3 | 51.3216 | September | 9 | September |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1800 | 10700 | 1800 | 0% | 76.98%
2023-03-05 | 14:00 | 2023-03-05 14:00 | 3 | March | 7.0104 | 522547.2 | 150529.4764 | 372017.7236 | 69984 | 16275.3488 | 4.3 | 4.3 | 69.984 | October | 10 | October |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1300 | 12000 | 1300 | 0% | 86.33%
2023-03-12 | 14:00 | 2023-03-12 14:00 | 3 | March | 7 | 597196.8 | 167889.8485 | 429306.9515 | 74649.6 | 17360.3721 | 4.3 | 4.3 | 74.6496 | November | 11 | November |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 1100 | 13100 | 1100 | 0% | 94.24%
2023-03-19 | 14:00 | 2023-03-19 14:00 | 3 | March | 7 | 671846.4 | 185250.2206 | 486596.1794 | 74649.6 | 17360.3721 | 4.3 | 4.3 | 74.6496 | December | 12 | December |  | 0 | 709171.2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 10555.3908 |  |  | 800 | 13900 | 800 | 0% | 100%
2023-03-26 | 14:00 | 2023-03-26 14:00 | 3 | March | 7 | 755827.2 | 204780.6392 | 551046.5608 | 83980.8 | 19530.4186 | 4.3 | 4.3 | 83.9808

## Control Panel (hidden)
Control Panel
Yes/No | Measurement Time | Volume Units | Annual/Monthly
Yes | Monthly | CCF | Monthly |  |  |  |  | 1 | January
No | Annually | 1k Gallons | Annual |  |  |  |  | 2 | February
[8 empty] | 3 | March
[8 empty] | 4 | April
Conversion Rates & Constants | [7 empty] | 5 | May
CCF to Gallons | [7 empty] | 6 | June
748.052 | [7 empty] | 7 | July
[8 empty] | 8 | August
[8 empty] | 9 | September
Water Efficiency Score Range | [7 empty] | 10 | October
Cycles | Score | [6 empty] | 11 | November
7 | 85.7143 | [6 empty] | 12 | December
6 | 83.3333 |  |  | > | <
5 | 80 |  | Green | 6
4 | 75 |  | Yellow | 2.5 | 5.999
3 | 66.6667 |  | Red | 2.5
2 | 50
1 | 0
| Treatment Cost Targets |  |  | Water & Sewer Cost Targets |  | Combined Cost Targets
| > | < |  | > | < | > | <
Green | 2.5 | 3.5 |  | 5 | 10 | 7.5 | 13
Yellow | 3.5 | 4.5 |  | 10.0001 | 13.0001 | 13 | 17.5
Red | 4.5 | 2.5 |  | 13.0001 | 5 | 17.5 | 7.5

## PivotCharts (hidden)
Row Labels | Monthly Treatment Spend per 1k gal MU | Makeup Ratio
January | 4.2867 | 3.0113
February | 3.1922 | 3.9428
March | 3.1326 | 4.3
April | #DIV/0! | #DIV/0!
Grand Total | 3.5372 | 3.7514
Row Labels | Sum of Monthly Water Treatment Spend2
January | 800
February | 700
March | 950
Grand Total | 2450
Row Labels | Sum of % of Total Budget Consumed | Sum of Target Consumption %
January | 0.057554 | 0.057554
February | 0.10791 | 0.11511
March | 0.17626 | 0.17986
April | 0 | 0.2518
May | 0 | 0.33094
June | 0 | 0.43165
July | 0 | 0.53237
August | 0 | 0.64029
September | 0 | 0.76978
October | 0 | 0.86331
November | 0 | 0.94245
December | 0 | 1
Grand Total | 0.34173 | 6.1151
| Row Labels | Sum of MU Useage (monthly)
| January | 186624
| February | 219283.2
| March | 303264
| Grand Total | 709171.2
| Row Labels | Monthly Treatment Spend per 1k gal MU | Monthly Utility Spend per 1k gal MU
| January | 4.2867 | 11.9109
| February | 3.1922 | 11.3455
| March | 3.1326 | 11.1937
| Grand Total | 10.6115 | 34.4501
|  | Row Labels | Sum of Change in Makeup | Sum of Change in Bleed
|  | 2023-01-08 | 51321.6 | 18329.1429
|  | 2023-01-15 | 55987.2 | 18060.3871
|  | 2023-01-22 | 37324.8 | 12040.2581
|  | 2023-01-29 | 41990.4 | 13545.2903
|  | 2023-02-05 | 51321.6 | 16555.3548
|  | 2023-02-12 | 60652.8 | 14105.3023
|  | 2023-02-19 | 55987.2 | 13020.2791
|  | 2023-02-26 | 51321.6 | 11935.2558
|  | 2023-03-05 | 69984 | 16275.3488
|  | 2023-03-12 | 74649.6 | 17360.3721
|  | 2023-03-19 | 74649.6 | 17360.3721
|  | 2023-03-26 | 83980.8 | 19530.4186
|  | Grand Total | 709171.2 | 188117.782

## Dashboard
2023-03-26 14:00
Enter your facility name here
Water Efficiency Dashboard
Water Efficienct Score (Concentration Rato) |  | Total Operating Cost / 1k gal of Makeup
4.3 | 8.262e-14% | 14.5378 | -10.25% | 3.1922
| Change from last reading |  | Change from month prior | Treatment Share (previous month)
| 3.4846 |  | 15.3009 | 11.3455
Most Recent Reading (Excellent >= 6.0) | Average (Year-to-Date) | Previous Month | Average (Year-to previous month) | Utility Share (previous month)